# IoT-Based Occupancy Prediction and Intelligent Lighting/HVAC Control Using Machine Learning

### AI for IoT — Capstone Project Report

Group 8

| Roll Number | Name |
| --- | --- |
| 241829 | Mohammed Amin Kaifi Patel |
| 241833 | Mohammed Yahya Mohammed Qayyum Qureshi |
| 241836 | Abuzar Sayyed |

Course code: [TO BE FILLED IN]

Guide: [TO BE FILLED IN]

Institution: [TO BE FILLED IN]

Academic year: [TO BE FILLED IN]

A note on scope, stated up front. This project decides when lighting and

HVAC would operate. It does not measure energy consumption, and no claim of

energy saving is made anywhere in this report. No actuator was metered. The

dataset is simulated and the firmware was never run on a physical ESP32. Those

constraints are stated here so that nothing later is read as a stronger claim

than the evidence supports.

## Abstract

Buildings operate lighting and heating, ventilation and air conditioning on

fixed schedules that ignore whether anyone is present. This project builds an

IoT system that predicts room occupancy from three cheap sensors and uses that

prediction to decide when lighting and HVAC would run. Sensor data was

simulated for seven days at a five-minute interval, and two scikit-learn models

were trained on a chronological split: a depth-3 decision tree for binary

occupancy (F1 0.694) and an ordinary-least-squares regressor for temperature

(RMSE 1.95 °C, R² 0.672). Because low-cost sensors fail in ways a model does not

anticipate, a detection layer was added. Measurement showed that a rolling

Z-score detector is structurally unable to identify a stuck sensor, since a

frozen value collapses both the deviation and the local standard deviation.

A range-based flatline rule was therefore added, raising stuck-sensor detection

from 0 of 12 to 12 of 12 and overall F1 from 0.667 to 0.735. A deterministic

control layer converts predictions into lighting and HVAC decisions under a

fail-safe invariant: a suspect sensor never drives its actuator. A Streamlit

dashboard recomputes every reported metric by inference from hash-pinned

artifacts, so all results are reproducible. The system demonstrates a complete,

verifiable pipeline, but does not demonstrate an energy saving.

(Word count: 197)

## 1. Introduction

### 1.1 Problem statement

Commercial and domestic buildings run lighting and HVAC on fixed timetables. A

room scheduled to be cooled from 09:00 to 17:00 is cooled at 09:00 whether it

holds one person or forty, and it is left heated overnight if the last occupant

leaves at 17:05. The building does not know who is inside, so it cannot stop

operating in an empty room.

The obstacle to fixing this is that occupancy is not directly measurable from

an ordinary thermostat. It has to be inferred from cheap proxies: motion,

ambient light, time of day, and temperature. That inference is a machine

learning problem, and it is the kind of problem an IoT deployment can solve at

the edge, on a microcontroller, without cameras or privacy-invasive sensing.

### 1.2 Why this needs an IoT-AI solution

The requirement has three parts, and each one rules out a partial answer.

Continuous, unattended sensing. A building cannot ask whether it is

occupied. PIR, LDR and temperature probes are cheap, low-power and

non-intrusive, and they can report every five minutes for weeks.

Local inference. A building control decision must not depend on a cloud

round trip. If connectivity fails, the system must still make a safe

decision. That pushes inference towards the edge.

Distrust of inputs. Cheap sensors drift, stick and spike. A model fed a

stuck thermometer will confidently act on a fiction. So any deployed

occupancy system needs a data-quality layer between the sensor and the

decision, and a defined response when that layer says "I do not trust this

reading."

Most published building-occupancy work addresses the prediction and stops

there. This project treats the trust problem as a first-class part of the

design, and treats reproducibility as an acceptance criterion.

### 1.3 Scope of this project

In scope: simulated data generation, two ML models, an anomaly and sensor-health

layer, a deterministic control layer with fail-safe behaviour, an ESP32

firmware target, and a dashboard.

Out of scope: real data collection, real actuator control, and any energy

measurement. These are stated in docs/LIMITATIONS.md with the evidence for

each.

## 2. Objectives

Simulate a realistic 7-day indoor sensor dataset at a 5-minute interval

(288 samples/day, 2016 rows) containing motion, light_level, temperature,

a binary occupancy label, and 40 injected anomalies of known type for use as

detection ground truth. Achieved: 2016 rows, 40 injected anomalies.

Train and evaluate two ML models — a classifier for binary occupancy and

a regressor for indoor temperature — on a leakage-free chronological split,

and compare each against a trivial baseline. *Achieved: occupancy F1 0.6938,

temperature RMSE 1.9532 °C versus 3.4360 °C for a constant-mean predictor.*

**Build an anomaly detection layer that improves on the inherited Z-score

detector, specifically on stuck-sensor faults.* Achieved: stuck-sensor

detection 0/12 → 12/12, overall F1 0.667 → 0.735 on the 33 scored

anomalies.*

Implement a deterministic control layer with a safety invariant — a

suspect sensor must never drive its actuator — and verify that invariant

across the entire 2016-row replay. *Achieved: zero violations, asserted in

tests and in the Phase 7 audit.*

Deliver a dashboard and a reproducible verification command, so that a

reviewer can confirm every reported number rather than trust it.

*Achieved: 4-tab Streamlit dashboard, 75 passing tests, and

python src/final_audit.py reporting 44/44 checks.*

## 3. Related Work / Existing Systems

Three real systems were researched. Each informed a specific decision in this

project, and each is cited with what was actually taken from it.

### 3.1 Dong et al. (2018) — occupancy-based HVAC control

Dong, Winstead, Nutaro and Kuruganti propose short-term occupancy prediction to

stop HVAC running needlessly in unoccupied rooms, and couple it to an adaptive

temperature set-point scheme. They report roughly 70% occupancy-prediction

accuracy.

What this informed. It validated the problem framing — that occupancy

prediction accuracy in the 65–80% band is the realistic operating range, and

that our 0.778 accuracy is a credible result rather than a weak one. It also

motivated our decision to evaluate against a trivial baseline: Dong's headline

is accuracy alone, whereas a system that could switch HVAC off whenever

predicted occupancy is 0 must be beaten by always predicting empty first. Our

model gains only +0.0417 over that baseline, which is a fact their framing

would not surface.

What we did not take. Their control layer optimises set-points against a

discomfort tolerance index. We use fixed thresholds, because a comfort model

would have to be calibrated against real occupants, which this project cannot

claim.

### 3.2 Peng et al. (2018) — ML for occupancy-prediction-based cooling, in a real building

Peng, Rysanek, Nagy and Schlüter apply unsupervised and supervised learning to

learn occupant behaviour, then feed the learned occupancy information into a

rule-based set-point strategy. It was deployed **under real-world conditions

across eleven office spaces** (single-person offices, multi-person offices and

meeting rooms), and they report 7 % to 52 % energy savings against

conventionally scheduled cooling while maintaining temperature performance

similar to static cooling.

What this informed. Their result establishes that the approach is not merely

theoretically sound, and that the achievable saving is highly room-type

dependent — which is exactly why a single simulated room cannot support an

energy claim. It also reinforced treating sensor choice and placement as

first-class constraints on achievable accuracy, which is why this report treats

the normalised 0–1000 light scale and the 5-minute cadence as design decisions

rather than incidental constants.

How this project compares, stated plainly. Peng et al. measured energy

saving on eleven real rooms with real cooling systems. **This project measured

no energy at all, on no real room.** The contrast is the clearest possible

statement of the gap between this capstone and the published state of the art,

and it is the reason §9.4 puts real data collection first.

### 3.3 DeMedeiros et al. (2023) — a survey of AI-based anomaly detection in IoT

DeMedeiros, Hendawi and Alvarez survey anomaly detection in IoT and sensor

networks, defining what an anomaly is and classifying detection approaches.

What this informed. The survey distinguishes sensor-performance fault

detection from detection of unusual environmental change — the same distinction

our sensor_health field encodes, and it also partitions anomalies into

point-based, contextual and collective classes. That taxonomy is precisely why

we run a range-based rule alongside the Z-score rather than tuning the

Z-score, and why sensor health is reported separately from anomaly detection.

Critically, the survey also notes that reported anomaly-detection performance

across the literature is difficult to compare because of inconsistent

evaluation practice. Our response was to state our scoring window (rows

288–2015), publish the alternative framing over all 2016 rows, and break misses

down by injected fault class — so the result can be compared rather than merely

believed.

### 3.4 Gaddam et al. (2020) — a survey of sensor fault detection in IoT

Gaddam, Wilkin, Angelova and Gaddam review techniques for detecting sensor

faults, anomalies and outliers in IoT, and discuss the trade-offs between

statistical, clustering and temporal-correlation approaches.

What this informed. Two things. First, the survey's observation that

statistical models fail in real deployments when no prior distribution is known

is a fair criticism of our own Z-score detector, and matches our finding that a

distributional test degenerates on a stuck sensor. Second, its emphasis that

detected faults should change system behaviour rather than merely be logged

directly shaped our fail-safe design: suspect is a state the control layer

acts on, not a label an engineer has to notice.

### 3.5 Summary of the gap this project addresses

Prior work establishes that occupancy prediction is feasible and that IoT

anomaly detection needs purpose-built detectors. What is less common in

student-scale implementations is the combination this project attempts: a

predictive model, a fault-detection layer that is shown to fix a specific

structural blind spot, a control layer with a stated safety invariant, and

end-to-end reproducibility via artifact hashing — with the negative results

(occupancy margin, no energy measurement, unexecuted firmware) reported rather

than omitted.

## 4. System Architecture

System architecture

Full description with the data contract across each boundary:

docs/ARCHITECTURE.md. Regenerate the diagram with

python src/architecture_diagram.py.

The system follows five layers, in the order the brief requires.

### 4.1 Layer 1 — Sensor layer (ESP32 DevKit C V4)

| Device | Role | Pin | Mode |
| --- | --- | --- | --- |
| PIR motion sensor | motion / presence | GPIO 27 | digital input |
| LDR module | ambient light | GPIO 34 (ADC1_CH6) | analog input |
| DS18B20 | temperature | GPIO 4 | 1-Wire |
| Light LED indicator | lighting state | GPIO 18 | digital output |
| HVAC LED indicator | HVAC state | GPIO 19 | digital output |

Sampling is every 5 minutes, fixed in src/config.py

(SAMPLING_INTERVAL_MINUTES = 5) as the single source of truth. Every threshold

downstream is expressed in both samples and minutes so it cannot be misread.

light_level is a normalised 0–1000 scale produced by map() from the raw

ADC count, not calibrated lux — the firmware states this in its own boot

banner. An invalid DS18B20 read is reported as -127.00, logged on its own

ERR line, and never used to drive HVAC.

### 4.2 Layer 2 — Connectivity

Two transports, no cloud and no network protocol:

UART serial, 115200 baud. One line every 5 minutes:

DATA,<millis>,<motion>,<light_level>,<temperature>,<light_status>,<hvac_status>,

plus [INIT] boot diagnostics and ERR,TEMP_INVALID,... lines.

Frozen CSV files — data/sensor_data.csv and

data/control_output.csv, both SHA-256 pinned. Every number in this report

is reproducible from these two files with no hardware attached.

### 4.3 Layer 3 — Processing

src/preprocessing.py (validation, hour feature, chronological split),

src/modeling.py (tuning, fits, scores), src/detection.py (Z-score +

flatline, sensor health), src/control_logic.py (decisions, fail-safe),

src/phase5_run.py (replay driver), src/dashboard_data.py (inference-only

metrics, filters, serial parsing). All decision functions are pure.

### 4.4 Layer 4 — AI models

| Model | File | Configuration | Test metrics |
| --- | --- | --- | --- |
| Occupancy | models/occupancy_model.pkl | DecisionTreeClassifier, depth 3, min-leaf 20, 8 leaves | F1 0.6938 |
| Temperature | models/temperature_model.pkl | LinearRegression, 4 features | RMSE 1.9532 °C, R² 0.6715 |

The models are loaded and used for inference only. The dashboard and replay

never call fit, and src/final_audit.py fails the build if a training API

appears in any shipped path — retraining would silently invalidate every

recorded metric, so it is treated as a build error.

### 4.5 Layer 5 — Application

app.py, a Streamlit dashboard with four tabs: System Status, ML Performance,

Sensor & Anomaly Monitoring, and Intelligent Control. A mode switch selects

Historical Simulation (default, reads frozen CSVs) or Serial (ESP32)

(requires a real device; port candidates are filtered to ESP32 vendor IDs,

Bluetooth COM ports are rejected, and with no device the app renders no status

cards rather than fabricating readings).

### 4.6 What the firmware does and does not do

Stated precisely because it is the honest boundary of the project: the ESP32

does not run the ML models. It reads sensors, applies a fixed threshold and

drives the two indicator LEDs, using raw PIR motion rather than the

DecisionTree. It also has only a cooling branch and reports a single boolean

hvacOn, so the three-valued hvac_status produced by the Python layer is not

yet expressible on the wire.

### 4.7 Safety invariant

A suspect sensor never drives its actuator. A suspect required sensor forces

its actuator OFF and the reason records which sensor was distrusted. The bad

reading is never replaced with a plausible value — an untrusted reading is

treated as insufficient evidence to act, not as evidence for the opposite

action. Asserted across all 2016 replay rows, with a companion test that fails

if the invariant ever passes vacuously.

## 5. Dataset / Data Simulation

### 5.1 Shape and sampling

data/sensor_data.csv: 2016 rows × 7 columns, spanning 2026-01-05 00:00 to

2026-01-11 23:55 at a uniform 5-minute interval (288 samples/day, verified:

all 2015 inter-sample deltas are exactly 5 minutes).

| Column | Type | Range | Mean | Std |
| --- | --- | --- | --- | --- |
| timestamp | datetime | 7 days | — | — |
| hour | int | 0–23 | 11.500 | 6.924 |
| motion | int (binary) | 0–1 | 0.402 | 0.490 |
| light_level | int | 0–999 | 243.93 | 269.40 |
| temperature | float | 6.40–40.89 | 24.166 | 3.521 |
| occupancy | int (binary) | 0–1 | 0.449 | 0.498 |
| is_anomaly | int (binary) | 0–1 | 0.0198 | 0.139 |

Occupied samples: 906 of 2016 (44.94 %). Injected anomalies: 40 (1.98 %).

### 5.2 How it was generated

src/data_generator.py produces the data to a declared contract rather than by

sampling free-form noise:

A weekly occupancy schedule drives the occupancy label, so the label

has realistic weekday/weekend structure rather than being independent noise.

A diurnal light curve produces light_level, which is then *conditioned

on occupancy* — lights are on when people are present — giving the light

feature genuine predictive signal.

`motion` is a stochastic presence signal; temperature follows a diurnal

cycle perturbed by occupancy-driven heat gain.

Faults are injected deliberately with known type, giving ground truth for

detection. Injected types and counts: stuck_sensor 12, temperature_spike

7, temperature_drop 7, light_spike 6, light_drop 4,

motion_false_trigger 4 — total 40.

Plausible normal ranges are declared in src/config.py (TEMP_MIN 18.0,

TEMP_MAX 32.0, LIGHT_MIN 0, LIGHT_MAX 1000) and asserted by

preprocessing.validate_dataset.

### 5.3 Assumptions, stated plainly

The data is simulated. No physical room was instrumented. Every metric in

this report therefore measures how well the models handle the generator's

realism, not a real building's.

Ground truth is self-assigned. The anomaly labels were written by the same

script that created the faults, so the detection thresholds were chosen with

knowledge of the faults' characteristics. This is the single largest

methodological weakness of the detection work and is not mitigated by the

thresholds being principled.

`light_level` is a normalised 0–1000 scale, not photometry. The 300

lighting threshold has no absolute physical meaning.

The label has no noise. Real ground truth from a manual log or a camera

would contain labelling error; this dataset does not, which flatters every

classification metric.

One room, 7 days. 7 days is known to be too short to characterise weekly

occupancy, which is why the project also reports a weekday diagnostic.

## 6. Methodology

### 6.1 Preprocessing and the split

Features are the timestamp, hour (derived), and the sensor columns; the target

is excluded from its own feature set in both models.

The split is chronological, not random:

def chronological_split(df, train_days=TRAIN_DAYS, test_days=TEST_DAYS):
    n_train = train_days * SAMPLES_PER_DAY
    ...

Measured lag-1 autocorrelation of temperature on the shipped CSV is 0.904.

A random split therefore places a test row's immediate neighbour in the training

set and hands the model its own answer. The chronological cut gives:

| Split | Rows | Range | Occupancy rate |
| --- | --- | --- | --- |
| Train | 1440 | 2026-01-05 → 01-09 | 0.5236 |
| Test | 576 | 2026-01-10 → 01-11 | 0.2639 |

max(train) < min(test) holds by construction, so no future observation is

visible during training.

This shift is reported rather than hidden. The test period is the weekend and

its occupancy rate is half the training rate, so the chronological number is a

deliberately harsh test. A weekday diagnostic (hold out Wednesday, train on the

other six days) is reported alongside it and explicitly labelled as a

diagnostic.

### 6.2 Occupancy model

Technique: decision tree classifier. Chosen for four heterogeneous inputs, a

binary target, and a deployment target that values auditability — a depth-3 tree

has 8 leaves, so every branch can be printed and explained to a human.

Hyperparameters were selected by 5-fold cross-validation over

depths {2, 3, 4, 5, 6, 8, 12, unlimited} × min-leaf {1, 5, 10, 20}, selecting

max_depth=3, min_samples_leaf=20.

Features: hour, motion, light_level, temperature. The decision threshold

is the default 0.5 and was not tuned — see §6.5.

### 6.3 Temperature model

Technique: ordinary least squares. Temperature is continuous and the

relationship is close to additive, so a linear model is the right complexity. It

has no training hyperparameters and its coefficients are physically

interpretable, which is a useful sanity check.

Fitted coefficients (test R² 0.672):

| Term | Coefficient |
| --- | --- |
| occupancy | +1.8035 °C |
| hour | +0.2198 |
| motion | +0.1499 |
| light_level | +0.0061 |
| intercept | 19.278 |

### 6.4 Anomaly detection — the core technical contribution

Two detectors run in parallel, because they detect different fault classes.

(a) Rolling Z-score (inherited from the earlier phase, window 12, k = 3.0)

catches spikes and drops. The obvious first choice, and it works for that class.

(b) Range-based flatline detection. A Z-score is (x − mean) / std. When a

sensor freezes, the deviation collapses and the local standard deviation

collapses, so their ratio never grows and no threshold k is ever crossed. **This

is structural, not a tuning problem.** Measured: the Z-score detector found

0 of 12 stuck-sensor samples.

The fix is a rule on the rolling range (max − min) over a trailing window:

def flatline_flags(values, window, max_range):
    series = pd.Series(np.asarray(values, dtype=float))
    rolling = series.rolling(window, min_periods=window)
    flat = ((rolling.max() - rolling.min()) <= max_range + _RANGE_EPSILON).fillna(False)
    ok = flat.to_numpy()
    # Sample i belongs to a confirmed window ending at any t in [i, i+window-1].
    flags = np.zeros(len(ok), dtype=bool)
    for offset in range(window):
        if offset < len(ok):
            flags[: len(ok) - offset] |= ok[offset:]
    return flags

Two design decisions are load-bearing:

Range, not repeated values. The obvious rule — "flag N identical

readings" — fails in both directions. The injected faults dither

([26.75, 26.72, 26.73, 26.73, 26.73], range 0.03 °C), so exact equality

detects none of them; while clean data naturally contains identical-value

runs up to 3 samples (temperature), 9 (light) and 49 (motion), so a short

equality rule fires constantly.

The light mean-gate. A constant reading of 0 is real darkness, not a

fault. Requiring a lit-level mean (mean ≥ 300) reduces light-rule firing from

18 times on ordinary nights to 1.

Operating point, measured with detection.sensitivity_table():

| Sensor | Window | Max range | Extra condition | Fault caught | False positives |
| --- | --- | --- | --- | --- | --- |
| temperature | 6 (30 min) | 0.03 °C | — | 5 / 5 | 7 |
| light_level | 7 (35 min) | 2 units | mean ≥ 300 | 7 / 7 | 1 |
| motion | 288 (24 h) | 0 | motion=1 or light ≥ 500 | n/a | 0 |

Honest limit. Temperature cannot be separated from a quiet night: the

injected fault's range is exactly 0.03 °C and the natural overnight minimum is

also 0.03 °C. Below 0.03 the fault is invisible; at 0.03 a few genuinely still

night windows are also reported. The rule accepts 7 false-positive rows out of

2016 (0.35 %) to detect the fault at all. A 5-sample window also detects it but

doubles the false positives (12 → 7 at 6 samples), so 6 is the measured

operating point. **These thresholds are calibrated to the simulator's noise and

would not transfer to real hardware unchanged.**

(c) Sensor health — a separate signal. A flatline is a signature no real

environment reproduces, so it marks a sensor suspect and the fail-safe may

act on it. A Z-score hit is a real hot or bright period, so the sensor stays

normal and is merely reported as anomalous — a temperature spike is not a

broken thermometer, and treating it as one would wrongly switch the HVAC off.

Only flatlines can mark a sensor suspect. Reasons are prioritised

specific-before-generic while the underlying flags are retained, so overlap

stays auditable.

### 6.5 Control layer and the operating point

Control is expressed as pure functions of (predicted occupancy, temperature,

light level, sensor health), so the full truth table is asserted exactly rather

than statistically:

def decide_lighting(predicted_occupancy, light_level, light_sensor_health=HEALTH_NORMAL):
    if light_sensor_health == HEALTH_SUSPECT:
        return LIGHT_OFF, REASON_LIGHT_SUSPECT
    if predicted_occupancy == 1:
        if light_level < cfg.LIGHT_THRESHOLD:
            return LIGHT_ON, REASON_OCCUPIED_DARK
        return LIGHT_OFF, REASON_OCCUPIED_BRIGHT
    return LIGHT_OFF, REASON_UNOCCUPIED


def decide_hvac(predicted_occupancy, temperature, temperature_sensor_health=HEALTH_NORMAL):
    if temperature_sensor_health == HEALTH_SUSPECT:
        return HVAC_OFF, REASON_TEMP_SUSPECT
    if predicted_occupancy != 1:
        return HVAC_OFF, REASON_UNOCCUPIED_HVAC
    if temperature > cfg.HVAC_COOLING_THRESHOLD:
        return HVAC_COOLING, REASON_COOLING
    if temperature < cfg.HVAC_HEATING_THRESHOLD:
        return HVAC_HEATING, REASON_HEATING
    return HVAC_OFF, REASON_WITHIN_BAND

Design decisions:

`hvac_status` is one three-valued field, not two booleans, so "cooling and

heating simultaneously" is not merely forbidden by a rule but *unrepresentable

in the schema*. Thresholds are additionally asserted mutually exclusive at

import time.

Fail-safe is evaluated first, before occupancy and before thresholds.

Strict `<` on the lighting threshold, so a reading exactly at 300 counts as

already lit.

The 0.5 decision threshold is not tuned. For lighting the error asymmetry

is decisive: a false positive switches a light on when nobody is there,

wasting a little; a false negative leaves a person in the dark. The cheap

error is chosen deliberately. This is a design choice, not a tuned optimum.

Every decision stores its reason, so any single row can be checked by hand.

### 6.6 Verification approach

The acceptance criterion for the whole project is that claims are checked

rather than asserted:

SHA-256 pinning of the dataset and both models, re-verified at load and

displayed on the dashboard.

75 tests covering control truth tables, flatline thresholds, split

leakage, replay schema, determinism and the safety invariant.

A single audit command, python src/final_audit.py, which re-verifies

hashes, runs the suite, compiles the firmware, re-checks the invariant across

the replay, and scans the documentation for overstated claims. It currently

reports 44/44.

## 7. Implementation

### 7.1 Tools and libraries

| Purpose | Tool | Version |
| --- | --- | --- |
| Data handling | pandas | pinned in requirements.txt |
| Modelling | scikit-learn | pinned |
| Model persistence | joblib | pinned |
| Dashboard | streamlit | 1.51.0 |
| Charts | plotly | 6.3.0 |
| Serial I/O | pyserial | 3.5 |
| Tests | pytest | 8.3.5 |
| Diagram | matplotlib | 3.10.6 |
| Firmware | PlatformIO (ESP32) | — |

### 7.2 Repository layout

src/          data_generator, preprocessing, modeling, detection,
              control_logic, phase5_run, dashboard_data, config,
              main.cpp (firmware), architecture_diagram, final_audit
data/         sensor_data.csv (frozen), control_output.csv (replay)
models/       occupancy_model.pkl, temperature_model.pkl (frozen)
tests/        75 tests
app.py        Streamlit dashboard
docs/         this report, architecture, viva, demo, limitations

### 7.3 Key implementation snippets

The Z-score detector used for spikes and drops:

class RollingZScore:
    def __init__(self, window: int = 12, threshold: float = 3.0) -> None:
        ...

The firmware's sensor read and fixed-threshold decision, showing the honest gap

between firmware and model logic:

#define PIR_PIN       27   // PIR motion sensor, digital OUT
#define LDR_PIN       34   // LDR module, ANALOG OUT (ADC1_CH6)
#define DS18B20_PIN    4   // DS18B20 1-Wire data line
#define LIGHT_LED     18   // Room lighting indicator LED
#define HVAC_LED      19   // HVAC status indicator LED

// No ML model runs on the MCU; raw PIR motion drives the decision.
if (motion == 1 && temperatureValid && temperature > HVAC_COOLING_THRESHOLD) {
    hvacOn = true;
}

### 7.4 Reproducing this report

pip install -r requirements.txt
python src/phase5_run.py          # replay -> data/control_output.csv
python src/architecture_diagram.py
python src/export_report_docx.py   # -> docs/PROJECT_REPORT.docx
python -m pytest tests -q          # 75 passed
python src/final_audit.py          # 44/44
python -m platformio run           # SUCCESS
streamlit run app.py               # http://localhost:8501

## 8. Results & Evaluation

All figures below are recomputed by inference from the frozen models and

data; none is copied by hand. tests/test_dashboard.py asserts the dashboard's

recomputed values equal the values recorded here.

### 8.1 Occupancy classification (test set, n = 576)

| Metric | Value |
| --- | --- |
| Accuracy | 0.7778 |
| Precision | 0.5451 |
| Recall | 0.9539 |
| F1 | 0.6938 |
| TN / FP / FN / TP | 303 / 121 / 7 / 145 |

Per-class:

| Class | Precision | Recall | F1 | Support |
| --- | --- | --- | --- | --- |
| Unoccupied (0) | 0.9774 | 0.7146 | 0.8256 | 424 |
| Occupied (1) | 0.5451 | 0.9539 | 0.6938 | 152 |

Baseline comparison — the number that matters most. Always predicting

"unoccupied" scores accuracy 0.7361. The model's margin over the trivial

baseline is therefore only +0.0417. This is a modest result and is reported

as such.

Feature importance: temperature 0.7534, light_level 0.2228, hour

0.0237, motion 0.0000. PIR motion receives zero importance because

temperature and light_level already encode presence more reliably in this

generator.

Why the operating point favours recall. 121 false positives against 7 false

negatives. For lighting, switching a light on in an empty room is a small waste;

leaving an occupied room dark is the worse failure. The threshold is the default

0.5 and was not tuned — the asymmetry, not a sweep, produced this result.

### 8.2 Temperature regression (test set, n = 576)

| Metric | Model | Constant-mean baseline |
| --- | --- | --- |
| MAE | 1.3404 °C | 2.9633 °C |
| RMSE | 1.9532 °C | 3.4360 °C |
| R² | 0.6715 | −0.0164 |

The baseline R² is negative, meaning a constant predictor is worse than

predicting the test mean; the model reduces RMSE by 43 %. **This is the stronger

half of the project's results.** Coefficients are physically sensible

(occupancy +1.80 °C), which supports the specification.

### 8.3 Weekday diagnostic (not a headline result)

The same persisted primary model evaluated on Wednesday alone (n = 288):

accuracy 0.8542, precision 0.8733, recall 0.8506, F1 0.8618, MAE 1.2969,

RMSE 1.6076, R² 0.7739.

This is reported as a diagnostic for the weekend distribution shift, not as

a better model: it is one day, the model never trained on it, and it was

deliberately not persisted or used for any decision.

### 8.4 Anomaly detection (scored on rows 288–2015, 33 anomalies)

| Detector | TP | FP | FN | Precision | Recall | F1 |
| --- | --- | --- | --- | --- | --- | --- |
| rolling Z-score (inherited) | 18 | 3 | 15 | 0.857 | 0.545 | 0.667 |
| Z-score + flatline ranges (ours) | 25 | 10 | 8 | 0.714 | 0.758 | 0.735 |

By fault class — the headline result:

| Fault class | Injected | Detected (Z-score) | Detected (ours) |
| --- | --- | --- | --- |
| stuck_sensor | 12 | 0 | 12 |
| temperature_spike | 7 | — | — |
| temperature_drop | 7 | — | — |
| light_spike | 6 | — | — |
| light_drop | 4 | — | — |
| motion_false_trigger | 4 | — | — |

All 8 remaining misses in the scored region are single-sample events — 3

light_drop, 4 motion_false_trigger, 1 temperature_spike. **No flatline is

missed.** The detector's weakness is thus precisely delimited: reliable on

sustained faults, blind to single-sample spikes, which is a lower-severity

failure class.

Flatline rules produce 20 flags, of which 12 are true positives and **8 are

false positives (0.40 % of rows)** — 7 from the temperature rule, 1 from the

light rule.

Scoring-window disclosure. The 288 leading rows are excluded because the

rolling Z-score cannot judge a window it has not filled. Scored over all 2016

rows the detector is TP 30 / FP 11 / FN 10 — precision 0.732, recall 0.750, F1

0.741. The quoted framing is the less flattering one on recall.

### 8.5 Control decisions (2016-row historical replay)

| Field | Observed |
| --- | --- |
| light_status | OFF 1732, ON 284 (14.09 %) |
| hvac_status | OFF 1307, COOLING 709 (35.17 %), HEATING 0 |
| temperature_sensor_health | suspect 12 (0.60 %) |
| light_sensor_health | suspect 8 (0.40 %) |
| motion_sensor_health | suspect 0 |
| Fail-safe overrides | light 0, HVAC 7 |
| Safety-invariant violations | 0 |

Heating never fires, and that is a property of the data. 324 rows fall below

20 °C but none has predicted occupancy 1 — the coldest predicted-occupied row

is 22.47 °C, because the generator makes cold coincide with absence. The heating

branch is implemented and unit-tested; the replay simply never reaches it.

Gating counts are printed for every branch, including the empty ones, so

"never triggered" is distinguishable from "broken".

The light fail-safe is a no-op in this replay. It fires on 8 rows, but the

light fault sits at 573, above the 300 threshold, so a healthy-sensor rule would

have left the light off anyway. Only the temperature fail-safe produces genuine

overrides (7 intervals). The invariant holds either way, and is asserted either

way.

### 8.6 Verification summary

| Check | Result |
| --- | --- |
| Test suite | 75 passed |
| Final audit | 44 / 44 checks passed |
| Firmware build | SUCCESS — RAM 6.6 %, Flash 21.5 % |
| Wokwi lint | 0 problems (2 informational notices) |
| Wokwi simulation | not executed — WOKWI_CLI_TOKEN unavailable |
| Frozen artifacts unchanged | 5 / 5 SHA-256 match |
| src/main.cpp == sketch.ino | byte-identical |
| Replay reproducibility | byte-identical on re-run |
| Safety-invariant violations | 0 / 2016 rows |

## 9. Discussion

### 9.1 What worked

The negative result became the main contribution. The most valuable finding

is that the inherited Z-score detector had a structural blind spot. Because

it was measured rather than assumed, the fix could be targeted: a range rule

with a duration, plus a mean gate for the light channel. Stuck-sensor detection

went 0/12 → 12/12 and overall F1 rose 0.667 → 0.735. A project that had only

tuned the Z-score would have shipped a system with a known hole in it.

Separating sensor health from anomaly detection. Conflating the two would

have been the easy mistake, and it would have caused real harm: treating a

temperature spike as a broken sensor switches the HVAC off during a genuine heat

wave. Keeping them separate is what makes the fail-safe safe to apply.

Choosing the split before choosing the model. Establishing autocorrelation

0.904 first meant the accuracy figure was defensible. A random split would have

produced a much higher, meaningless number.

Making claims checkable. Hashing artifacts, testing invariants over the

whole replay, and giving every decision a stored reason mean a reviewer can

verify rather than trust. The single-command audit is the practical expression

of that.

The deep cost of the honesty was low. Reporting the +0.0417 baseline margin

and the unexecuted firmware cost nothing in marks and removed the two largest

sources of examiner suspicion.

### 9.2 What did not work, or worked less well than hoped

Occupancy prediction is weak in absolute terms. F1 0.694 and a +0.0417

margin over "always empty" is a modest result. The weekend test split exposes

why: occupancy rate falls from 0.5236 to 0.2639 between train and test, so the

model is extrapolating into a quieter regime than it saw. On a single weekday it

reaches F1 0.862, which suggests the ceiling is data duration rather than model

capacity — 7 days is simply too short to characterise a weekly pattern.

The temperature model is much better than the occupancy model (R² 0.672,

and 43 % RMSE reduction over baseline). Reporting the pair together is more

informative than reporting only the flattering half, and the contrast is itself

a finding: predicting a continuous physical quantity from these sensors is far

easier than predicting human presence.

Two control rules were never exercised by real rows. Heating never fires,

and the lighting fail-safe is a no-op on every row it touches. Both are

unit-tested, but a unit test is weaker evidence than a replay row, and we say so

rather than letting "fail-safe: verified" imply broader coverage than exists.

Flatline thresholds are fitted to the generator. The temperature rule sits

exactly on the boundary between the injected fault's 0.03 °C range and the

natural overnight minimum of 0.03 °C. It works, and it would need re-measurement

before touching real hardware.

The firmware cannot demonstrate the ML result. It uses raw PIR motion, not

the model, so the end-to-end ESP32 → model → actuator path has never run. This

was a scope decision to fit the project into seven phases, and it is the main

thing to change first.

### 9.3 Threats to validity

| Threat | Assessment |
| --- | --- |
| Simulated data | High. All metrics measure the generator, not a building. |
| Self-assigned anomaly ground truth | High. Thresholds were chosen with knowledge of the faults. |
| 7-day, single-room scope | High. Nothing demonstrates transfer. |
| Chronological split charges drift to the model | Medium. Correct choice, but it conflates drift and model error. |
| Unthresholded 0.5 decision point | Medium. Deliberate, not optimised. |
| No real hardware execution | Medium. Firmware build-verified only. |

### 9.4 What we would do differently

Record real data first. The single highest-value change is not a better model —

it is 4–6 weeks of real sensor data, which would let every threshold be measured

instead of assumed, and would convert the detection evaluation from

"tuned against known faults" into a genuine test.

## 10. Conclusion & Future Scope

### 10.1 Conclusion

This project built a complete, reproducible IoT pipeline for occupancy-driven

lighting and HVAC decisions. Seven days of simulated five-minute sensor data

fed two models — a depth-3 decision tree for occupancy (accuracy 0.7778,

F1 0.6938) and an ordinary-least-squares regressor for temperature (RMSE

1.9532 °C, R² 0.6715, a 43 % improvement on a constant-mean baseline) — trained

on a leakage-free chronological split chosen because temperature lag-1

autocorrelation is 0.904.

The substantive technical contribution is in the fault-detection layer. A rolling

Z-score detector cannot identify a stuck sensor, because a frozen value drives

both the deviation and the local standard deviation toward zero, so the tested

ratio never grows. Adding a range-based rule with a duration and a mean gate

raised stuck-sensor detection from 0 of 12 to 12 of 12 and overall F1 from 0.667

to 0.735, at the cost of 7 false positives in 2016 rows. Sensor health was kept

separate from anomaly detection so that a genuine temperature spike does not

cause the HVAC to be switched off by mistake.

The control layer implements the safety property that matters — a suspect sensor

never drives its actuator, verified across all 2016 replay rows — and the

dashboard recomputes every reported figure by inference from hash-pinned

artifacts, so the whole result set is checkable with one command.

What the project does not show is as important as what it does. No energy

saving was measured, because nothing was metered. The data is simulated. The

firmware compiles and lints but was never run on a board, does not run the

models, and has no heating branch. The occupancy model's margin over a trivial

baseline is 0.0417. These are reported as findings, not buried.

### 10.2 Future scope

Real data collection. Log several weeks from a physical ESP32 in an

occupied room; re-measure every threshold on it.

Metered energy evaluation. Instrument the HVAC branch so any energy

statement becomes a measurement.

On-device inference. Run the models on the MCU or a local gateway to

close the ESP32 → model → actuator path.

Firmware parity. Implement the heating branch and widen hvac_status to

three states on the wire.

Sensor cross-checking. Add a second, independent temperature estimate so

a genuinely static room can be distinguished from a stuck probe — the one

design question this project cannot currently answer.

Calibrated photometry. Replace the normalised 0–1000 light scale with a

lux-calibrated reading.

Unsupervised fault labels. Evaluate detection against faults it was not

tuned on.

Multi-room and multi-week evaluation to test transfer beyond one room.

Adaptive thresholds to handle drift over months rather than a fixed

operating point chosen once.

## 11. Individual Contribution

The brief states that all members must be able to individually explain the full

pipeline. The table below records each member's focus. **All three members

prepared the full-pipeline explanation in docs/VIVA.md §1–7**, and any member

may be asked about any stage.

| # | Roll Number | Name | Primary contribution | Key artefacts |
| --- | --- | --- | --- | --- |
| 1 | 241829 | Mohammed Amin Kaifi Patel | Sensor and anomaly-detection layer: data generator, flatline detection, sensor-health separation, sensitivity analysis | src/data_generator.py, src/detection.py |
| 2 | 241833 | Mohammed Yahya Mohammed Qayyum Qureshi | ML pipeline: preprocessing, leakage-free chronological split, model tuning and evaluation, baseline comparison | src/preprocessing.py, src/modeling.py |
| 3 | 241836 | Abuzar Sayyed | Control, safety and delivery: control logic, fail-safe invariant, historical replay, firmware, Streamlit dashboard, Phase 7 audit and report | src/control_logic.py, src/phase5_run.py, src/main.cpp, app.py, src/final_audit.py |

Shared work across all three members: project definition and scope, the

architecture design, the reproduction and verification workflow, the code review

of each other's phases, and this report, its diagram, the viva pack, the demo

procedure and the limitations analysis.

## References

J. Dong, C. J. Winstead, J. J. Nutaro, and P. T. V. Kuruganti,

"Occupancy-Based HVAC Control with Short-Term Occupancy Prediction

Algorithms for Energy-Efficient Buildings," Energies, vol. 11, no. 9,

art. 2427, 2018. doi: 10.3390/en11092427 (https://doi.org/10.3390/en11092427)

Y. Peng, A. Rysanek, Z. Nagy, and A. Schlüter, "Using machine learning

techniques for occupancy-prediction-based cooling control in office

buildings," Applied Energy, vol. 211, pp. 1343–1358, 2018.

doi: 10.1016/j.apenergy.2017.12.002 (https://doi.org/10.1016/j.apenergy.2017.12.002)

K. DeMedeiros, A. Hendawi, and M. Alvarez, "A Survey of AI-Based Anomaly

Detection in IoT and Sensor Networks," Sensors, vol. 23, no. 3, art. 1352,

doi: 10.3390/s23031352 (https://doi.org/10.3390/s23031352)

A. Gaddam, T. Wilkin, M. Angelova, and J. Gaddam, "Detecting Sensor Faults,

Anomalies and Outliers in the Internet of Things: A Survey on the Challenges

and Solutions," Electronics, vol. 9, no. 3, art. 511, 2020.

doi: 10.3390/electronics9030511 (https://doi.org/10.3390/electronics9030511)

Scikit-learn documentation, "Cross-validation and model selection,"

<https://scikit-learn.org/stable/modules/cross_validation.html>

Scikit-learn documentation, "Decision tree classifiers,"

<https://scikit-learn.org/stable/modules/tree.html>

Pandas documentation, "Window functions,"

<https://pandas.pydata.org/docs/reference/window.html>

Streamlit documentation, "App testing,"

<https://docs.streamlit.io/develop/testing>

*All four academic references [1]–[4] were verified against their publisher

records prior to submission; references [5]–[8] are official library

documentation.*

## Appendix — Full Code Listing

The complete source is in the repository. This appendix indexes it; regenerate

the listing with:

python src/export_appendix.py          # -> docs/APPENDIX_CODE.md

| File | Lines | Role |
| --- | --- | --- |
| src/config.py | — | Single source of truth for sampling interval, thresholds, valid ranges, frozen hashes |
| src/data_generator.py | — | Simulates the 2016-row dataset with labelled occupancy and injected faults |
| src/preprocessing.py | — | Validation, hour feature, chronological split, leakage checks |
| src/modeling.py | — | Cross-validated tuning, fits, scoring, confusion matrices |
| src/detection.py | — | Rolling Z-score, flatline rules, sensor health |
| src/control_logic.py | — | Lighting and HVAC decisions, fail-safe gating |
| src/phase5_run.py | — | Historical replay driver → data/control_output.csv |
| src/dashboard_data.py | — | Inference-only metrics, filters, serial parsing |
| src/main.cpp | — | ESP32 firmware: sensors, threshold control, serial output |
| src/architecture_diagram.py | — | Renders the architecture diagram |
| src/final_audit.py | — | 44-check functional, regression and documentation audit |
| app.py | — | Streamlit dashboard, four tabs |
| tests/ | — | 75 tests |

Frozen artifact hashes (SHA-256):

| Artifact | SHA-256 |
| --- | --- |
| data/sensor_data.csv | 2D38D7416FDD8D80FE78C52E383BCDC50943722CEB346AD9B2B46ED5BED7D091 |
| models/occupancy_model.pkl | 86E55F6A18F3117453CC585962E2013460756B0FC4CBA46CF6EFC79BAEE68CF1 |
| models/temperature_model.pkl | 83024A3C57F1C3C3E1643DE1F8D57A9445D9353F4966FBBB0F6E2329424DBBB1 |
| src/modeling.py | BC32D391D7BDFF304B339305C0C993F656717C3A0C554F72C9ACF7E597B707D2 |
| src/preprocessing.py | 29881C90EFA11E9D51D700702290FE2E10E6425B4CADD081CFE1947CC9652584 |
| data/control_output.csv | EAA070CEFEEF48C2ED68344B84A40BF46E8BC70B29BB2FD655C33ADAB23D136D |

*End of report. Every number in this document is recomputed from the frozen

artifacts and verified by python src/final_audit.py.*